## Certificate
This is to certify that a Fire Risk Assessment has been carried out for:
Chearsley Village Hall
Winchendon Road, Chearsley, Buckinghamshire, HP18 0DP
2018-05-16
In accordance with The Regulatory Reform (Fire Safety) Order 2005
Fire Risk Management
Certificate
of
Fire Risk Assessment
Telephone: 0845 602 8170
Email: customer.service@nfrac.co.uk
Web: www.nfrac.co.uk

## Cover
Winchendon Road, Chearsley, Buckinghamshire, HP18 0DP
2018-05-16
Chearsley Village Hall
Fire Risk
Assessment Report
Telephone: 0845 602 8170
Email: customer.service@nfrac.co.uk
Web: www.nfrac.co.uk

## RA Part 1
FIRE RISK ASSESSMENT
Chearsley Village Hall
Winchendon Road, Chearsley, Buckinghamshire, HP18 0DP
Assessor: |  | Dave Perkins MIFPO MInstLM
Telephone : 07590224225
2018-05-16
Nature of occupancy: |  |  |  | Place of Entertainment
Use of remainder of building |  |  |  | Pre-School
Construction of buildings |  |  |  | A detached, brick & blockwork, windowed property with pitched roof.
Location of workplace in buildings |  |  |  | All areas
Total number of floors. |  |  |  | 1
No of staircases available as exit route |  |  |  | Nil
No of final exits |  |  |  | 3
No of employees in workplace |  |  |  | Nil (Varying Volunteers)
No of other persons in workplace |  |  |  | Undefined
Persons under 18 in workplace |  |  |  | Undefined (Nil Employed)
Disabled Occupants |  |  |  | Undefined (Nil Employed)
Responsible person(s) |  |  |  | Antonia Stratford
Point of Contact |  |  |  | Martin Hearmon
FRA completed by |  |  |  | Dave Perkins MIFPO MInstLM
Proposed Review date |  |  |  | 2019-05-01
Other relevant information
BUILDING/PREMISES RISK PROFILE (in accordance with BS 9999 2008)
The purpose of the Building Premises Risk Profile is so that the assessor can determine the adequacy of the fire safety management levels
Table 1 - Occupant risk category
Risk category | Description |  |  | Examples
A | Occupants who are awake and familiar with the building |  |  | Office and industrial premises
B | Occupants who are awake and unfamiliar with the building |  |  | Shops, exhibition, museums, educational establishments, other assembly buildings
C | Occupants who are likely to be asleep |  |  | Residential
Ci | Long term individual occupancy |  |  | Individual flats without 24hr maintenance and management control on site
Cii | Long term managed occupancy |  |  | Serviced flats, halls of residence, sleeping areas and boarding schools
Ciii | Short term occupancy |  |  | Hotels
D | Occupants receiving medical care |  |  | Hospitals
E | Occupants In transit |  |  | Railway Stations, airports
Table 2 - Fire Growth Rate (FGR)
Category | FGR | Examples
1 | Slow | Open Plan office, limited combustible materials
2 | Medium | Stacked cardboard boxes, wooden pallets
3 | Fast | Baled thermoplastic chips, stacked plastic products, baled clothing
4 | Ultra fast | Flammable liquids, expanded cellular plastics and foam
Table 3 - Risk Profile
Category |  | FGR | Risk Profile |  | Examples
A | 1 | Slow | Occupants who are awake and familiar with the building |  | Open-sided car park
| 2 | Medium |  |  | Office
| 3 | Fast |  |  | Filing Room,
| 4 | Ultra fast |  |  | Plant room
B | 1 | Slow | Occupants who are awake and unfamiliar with the building |  | Reception area
| 2 | Medium |  |  | Bar, Gymnasium
| 3 | Fast |  |  | Shop
| 4 | Ultra fast |  |  | xxx
C | 1 | Slow | Occupants who are likely to be asleep |  | House Conservatory,
| 2 | Medium |  |  | Hotel bedroom,
| 3 | Fast |  |  | hotel store room
| 4 | Ultra fast |  |  | XX
The Risk Profile for these premises is | [6 empty] | B1
The fire safety management levels for these premises are considered to be: |  |  |  | Adequate
Not Adequate
RISK LEVEL ESTIMATOR
Potential consequences of fire → Fire hazard ↓ |  | Slight harm |  | Moderate harm |  | Extreme harm
LOW |  | Trivial risk |  | Tolerable risk |  | Moderate risk
MEDIUM |  | Tolerable risk |  | Moderate risk |  | Substantial risk
HIGH |  | Moderate risk |  | Substantial risk |  | Intolerable risk
Taking into account the fire prevention measures observed at the time of this risk assessment, it is considered that the hazard from fire (probability of ignition) at this building is
| LOW |  | MEDIUM |  |  | HIGH
Taking into account the nature of the building and the occupants, as well as the fire protection and procedural arrangements observed at the time of this risk assessment, it is considered that the consequences for life safety in the event of fire would be:
SLIGHT HARM |  |  | MODERATE HARM |  |  | EXTREME HARM
In this context, a definition of the above terms is as follows:
Slight harm: |  | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a bedroom in which a fire occurs).
Moderate harm: |  | Outbreak of fire could result in injury of one or more occupants, but it is unlikely to involve multiple fatalities.
Extreme harm: |  | Significant potential for serious injury or death of one or more occupants.
Accordingly, it is considered that the risk to life from fire at this building is:
TRIVIAL TOLERABLE MODERATE SUBSTANTIAL INTOLERABLE
Risk-Based Control Plan
Risk Level |  | Action and timescale
Trivial |  | No action is required and no detailed records need be kept.
Tolerable |  | No major additional controls required. However, there may be a need for consideration of improvements that involve minor or limited cost.
Moderate |  | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment may be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
Substantial |  | Considerable resources may have to be allocated to reduce the risk. If the building is unoccupied, it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
Intolerable |  | Building (or relevant area) should not be occupied until the risk is reduced.
Action Plan
It is considered that the recommendations should be implemented in order to reduce fire risk too, or maintain it at, the following level:
TRIVIAL |  |  |  | TOLERABLE
Assessors Comments
In accordance with The Building Regulations 2000: Approved Document B Fire Safety the premise should not exceed 200 persons for the premise purpose group, the footprint of the structure and the exits available. The occupancy level should be controlled and not exceed this figure.
However consideration should be given to the amount of seating that can be sited. The amount of seats will determine the true figure of occupancy. If the seating levels are less than the Licenced figure then the lowest occupancy level should be adopted.

## RA Part 2
FIRE RISK ASSESSMENT
COMPANY: |  | Chearsley Village Hall
LOCATION: |  | Winchendon Road, Chearsley, Buckinghamshire, HP18 0DP
ASSESSOR: |  | Dave Perkins MIFPO MInstLM
DATE: |  | 2018-05-16
IGNITION SOURCES |  |  |  | Report Reference Number
Smoking - adequate policy & controls? |  |  | Y | A
Safe use of portable/radiant heaters |  |  | Y
Are there reasonable measures to prevent fires of electrical origin? |  |  | Y
Is electrical equipment in a satisfactory condition (PAT testing?) |  |  | N | Reference 4
Is there evidence of electrical circuit overloading (Ext leads/ adaptors)? |  |  | N
Is there a policy regarding the use of personal electrical appliances? |  |  | N | Reference 5
Are there adequate arrangements for disposal of flammable waste? |  |  | Y
Are there any works in progress that could cause ignition ? |  |  | N
Are light bulbs/electrical appliances & fittings near combustible materials ? |  |  | Y | Reference 1
Cooking appliances - cleaning of filters and ducting? |  |  | Y | Reference 6
Contractors (external & in house) policy and controls (Hot work permits?) |  |  | N | Reference 34
Are there arrangements for maintenance of plant, boilers & major appliances? |  |  | Y
Is there adequate lightning protection? |  |  | N | Reference 7
Have Gas installations been checked in the last year ? |  |  | N/A
Have electrical installations been checked in the last 5 years? |  |  | Y | Reference 8
A. No smoking premises
COMBUSTIBLE MATERIALS/FLAMMABLE LIQUIDS |  |  |  | Report Reference Number
Are combustible materials stored in a safe location ? (Fire loading control) |  |  | Y
Are furnishings in good condition/compliance with furnishing regulations |  |  | Y
Are flammable substances gases/liquids used & stored correctly ? |  |  | N/A
Are DSEAR applicable (Risk Assessment in place) |  |  | N/A
MEASURES TO LIMIT FIRE SPREAD |  |  |  | Report Reference Number
Do walls/ceilings have combustible coverings ? |  |  | N
Is there adequate fire stopping (concealed spaces/wall penetrations) ? |  |  | N | Reference 2 & A
Are there adequately protected routes/reasonable compartmentation ? |  |  | Y | A
Are fire dampers provided (reasonable provision - as far as can be ascertained) |  |  | N/A
Is there adequate provision to restrict the spread of fire and smoke |  |  | Y | Reference 9
A. Based on a visual inspection of readily accessible areas with a degree of sampling where appropriate.
.
MEANS OF ESCAPE FROM FIRE |  |  |  | Report Reference Number
Are their adequate & suitable Means of Escape ? |  |  | Y
Do critical doors open in the direction of escape where necessary? |  |  | Y
Are escape routes free from obstruction (internally & externally) ? |  |  | N | Reference 3
Are all travel distance requirements met? (single & alternate MOE) |  |  | Y
Do external stairways, platforms, ladders etc. appear in good condition? |  |  | N/A
Are escape routes free of combustible materials/electrical appliances? |  |  | Y
Is the use of sliding and revolving doors as means of escape avoided? |  |  | Y
Are exits easily openable where necessary? |  |  | Y
Are surfaces in good condition, free from trips, slip hazards? |  |  | Y
Are normal lighting levels adequate? |  |  | Y
Reasonable standard of emergency lighting provided? |  |  | N | Reference 10-11 & A
Reasonable standard of fire safety signs and notices? |  |  | N | Reference 12
Are there required arrangements for inner rooms? |  |  | Y
A. Based on visual inspection, but no test of luminance levels or verification of full compliance with relevant British Standards carried out.
FIRE RESISTING DOORS |  |  |  | Report Reference Number
Are effective self-closing, hold open, devices fitted, where necessary? |  |  | Y
Do doors fit correctly to adequate rebates? (Full self closure) |  |  | Y
Are smoke or heat seals fitted? |  |  | N | Reference 13
Do fire doors appear to be in good condition |  |  | Y
Are 'fire door' notices fitted on fire doors? |  |  | N | Reference 14
Is the building free of wedged/open fire doors? |  |  | Y
Are fire doors indicated 'keep locked shut' secured/locked |  |  | Y
FIRE DETECTION & ALARMS |  |  |  | Report Reference Number
Reasonable manually operated electrical fire alarm system provided? |  |  | Y | A
Are adequate alarm call points provided? |  |  | Y
Are call points/detectors accessible/unobstructed |  |  | Y
Is automatic fire detection installed |  |  | Y
Extent automatic fire detection generally appropriate to risk & occupancy |  |  | Y
Adequate Control and indicating equipment |  |  | N | Reference 15-16
Is the System linked to remote manned centre |  |  | N | Reference 35
A. Based on visual inspection, but no audibility tests or verification of full compliance with relevant British Standards carried out.
FIRE FIGHTING FACILITIES |  |  |  | Report Reference Number
Is there sufficient equipment commensurate with risk? |  |  | Y
Is equipment located correctly & identifiable ? |  |  | N | Reference 17
Does fire fighting equipment appear functional |  |  | Y
Is site access suitable for emergency services? |  |  | Y
Is any Fixed Fire Suppression installed |  |  | N
Suitable provision of fire-fighters switches (i.e. HV luminous tubes etc) |  |  | N/A
FIRE SAFETY MANAGEMENT & FIRE EVACUATION |  |  |  | Report Reference Number
Competent person/fire safety manager appointed? |  |  | Y | A
Are the fire safety management levels at the required standard? |  |  | Y | .
Is there an established Fire Policy /Fire Plan? |  |  | N | Reference 18
Suitable arrangements for calling fire services |  |  | Y
Suitable arrangements for meeting fire services (provision of information) |  |  | Y
Suitable arrangements for ensuring premises have been evacuated |  |  | Y
Is the assembly point clearly marked? (when allowed) |  |  | Y | Reference 19
Adequate procedures for evacuation/assisting occupants with disabilities? |  |  | N | Reference 20
Arrangements for inspecting building at end of day? (written) |  |  | N | Reference 21
Is there Evacuation Lifting Equipment on site? |  |  | N
Routine in house fire inspections. (written) |  |  | N | Reference 22
Appropriate liaison with Fire Brigade? |  |  | Y
A. This is not intended to represent a legal interpretation of responsibility, but merely reflects the managerial arrangement in place at the time of the risk assessment.
ARSON REDUCTION |  |  |  | Report Reference Number
Has the building got CCTV cameras/security alarm? |  |  | Y
Does basic security against arson appear reasonable |  |  | Y | Reference 36 & A
Are skips, bins and other fire loading kept at distance from main building? |  |  | Y
Is there a regular collection of rubbish? |  |  | Y
Are gas cylinders stored in a locked caged area away from building? |  |  | N/A
A. Reasonable only in the context of this fire risk assessment. If specific advice on security (including security against arson) is required, the advice of a security specialist should be obtained.
.
FIRE SAFETY TRAINING |  |  |  | Report Reference Number
Is there a procedure for the training of new arrivals? |  |  | N | Reference 23
Are all other staff periodically trained ? (Refresher training) |  |  | N | Reference 24
Does staff training include:
| Fire risks on the premises? |  | N | Reference 24
| fire safety measures in the building? |  | N | Reference 24
| Action in the event of fire? |  | N | Reference 24
| Action on hearing the fire alarm? |  | N | Reference 24
| Location and use of fire equipment? |  | N | Reference 24
| Means of summoning fire brigade? |  | N | Reference 24
| Identity of persons nominated to assist with evacuation? |  | N | Reference 24
| Identity of persons nominated to use fire extinguishers? |  | N | Reference 24
Are staff with special responsibilities given additional training? |  |  | N | Reference 24
Are regular fire drills carried out ? |  |  | N | Reference 25
TESTING & MAINTENANCE |  |  |  | Report Reference Number
Are the required regular tests and maintenance carried out on:
| fire detection and alarm systems |  | N | Reference 26-27
| emergency lighting system |  | N | Reference 28-29
| fire extinguishers and hose reels |  | N | Reference 30
| automatic sprinkler systems |  | N/A
| other fixed suppression systems |  | N/A
| automatic closing doors & shutters |  | N | Reference 31
| evacuation & fire fighting lifts |  | N/A
| rising Mains |  | N/A
| escape stairs |  | N/A
| fire doors (register maintained) |  | N | Reference 32
| final exit doors/security fastenings |  | N | Reference 32
| Evacuation Lift Equipment |  | N/A
| lightning protection |  | N/A
RECORDS |  |  |  | Report Reference Number
Appropriate records of:
| Fire training |  | N | Reference 33
| Fire Drills |  | N | Reference 33
| Fire alarm tests |  | N | Reference 33
| Emergency lighting system tests |  | N | Reference 33
| Fire Extinguishers & other fixed suppression systems |  | N | Reference 33

## RA Part 3
FIRE RISK ASSESSMENT
COMPANY: |  | Chearsley Village Hall |  |  |  |  | FRA 1 Annual Inspection
LOCATION: |  | Winchendon Road, Chearsley, Buckinghamshire, HP18 0DP |  |  |  |  | FRA 2 - Review
ASSESSOR: |  | Dave Perkins MIFPO MInstLM |  |  | Tel: 07590224225
DATE |  | 2018-05-16
Ref | Site Location | Workplace Fire Hazard | Persons at Risk | C | Risk Evaluation | Further Action |  | Remarks | Priority
1 | Electrical Cupboard | It was noted that the electrical cupboard contained combustibles. | Staff/Visitors | 1 | Critical | Combustibles combined with the heat and electrical risk in the electrical cupboard makes any such practice a high risk. It should be ensured this area is cleared of all storage. It should then be ensured this area is secured to prevent unauthorised access. As the area has a dual purpose of utilities and storeroom it is recommended that either the utilities are compartmented from the storage area or as a minimum a management policy should be initiated to ensure all storage remains at least 1m from any utilities. |  | Management Procedure | Priority 1 Immediate
2 | Electrical Cupboard | The compartment fire walls in the Electrical Cupboard required compartmentation and smoke stopping. | Staff/Visitors | 1 | Critical | The compartment fire walls in the Electrical Cupboard should be constructed of materials giving a minimum of 30 minutes fire resistance. The ceiling and walls should be imperforate except where services pass through and these must be effectively fire stopped. |  | Management Procedure | Priority 1 Immediate
3 | Pre-School | The main entry/exit to the Pre-School is an escape route however it contained combustibles and obstructions. It is recommended the area adjacent the main entry/exit to the Pre-School is kept clear. | Staff/Visitors | 1 | Critical | Refuse, combustible storage and obstructions should not be allowed to accumulate in any of the exit routes in the premise this includes electrical items. Clear and direct exit routes should be maintained clear at all times. It is recommended the area adjacent the main entry/exit to the Pre-School is cleared of all refuse, combustible storage and obstructions. The area leading to and around the exit should be the minimum of the fire exit width. |  | Management Procedure | Priority 1 Immediate
4 | All Areas | The electrical safety testing (PAT) of electrically powered appliances is required. | Staff/Visitors | 2 | High | It is recommended by the ‘Electricity at Work Regulations’ that the electrical safety testing (PAT) of all electrically powered appliances and associated equipment continues at appropriate intervals. (You may refer to HSE guidance, ‘maintaining portable electrical equipment in offices and other low risk environments’). Documentation is required to be held on site in the Fire Logbook. |  | Management Procedure | Priority 2 1 Month
5 | All Areas | It is recommended there should be a written policy regarding the managerial control of mains-powered electrical items of equipment that are brought into the premises. | Staff/Visitors | 2 | High | All such items should be included in the periodic electrical safety testing before permission is given for their use on the premises. The building policy regarding the use of personal electrical equipment should be maintained in a written format and highlighted in the building induction and on-going awareness training. |  | Management Procedure | Priority 2 1 Month
6 | Kitchen | Although recently installed it should be ensured the oven and other catering equipment is regularly checked for defects and is cleaned regularly with documentation held on-site. | Staff/Visitors | 2 | High | The oven and other catering equipment should continue to be regularly cleaned dependant on their use. Details should be recorded in the Fire Logbook in order to confirm to the statutory authorities, which will also include Environmental Health that a cleaning regime is in place and adhered to. The person carrying out the various tasks detailed above should sign the Fire Logbook confirming that they have been fully completed. |  | Maintenance | Priority 2 1 Month
7 | All Areas | No lightning conductor for the building was evident. | Staff/Visitors | 2 | High | No lightning conductor for the building was evident. This creates a risk of faulty earth integrity with the potential for serious building damage or fire and a risk to life safety. A lightning conductor is not required on a small premise as they are deemed as a low risk, however, if concerns are raised a lightning risk assessment can be carried out in accordance with BSEN 62305/2 2008 to ascertain whether or not lightning protection is required. |  | Management Procedure | Priority 2 1 Month
8 | All Areas | The main electrical system has been installed recently however no documentation was available. | Staff/Visitors | 2 | High | In accordance with IEE Regulations, a competent Electrical Engineer should test the electrical system periodically and the results of these tests should be recorded. Documentation is required to be held on site in the Fire Logbook. |  | Maintenance | Priority 2 1 Month
9 | Kitchen | The kitchen is provided with a serving hatch with a fire shutter installed to provide a barrier against the spread of fire between areas of the building in order to limit damage to the building however it should be confirmed the shutter is linked to the fire alarm system or operated by fusible links. | Staff/Visitors | 2 | High | Kitchens provided with a serving hatch are to have a fire shutter installed to provide a barrier against the spread of fire between areas of the building in order to limit damage to the building. The shutter is required to be either linked to a fire alarm for automatic closure in the event of a fire or operated by fusible links. It is also recommended that objects are not placed beneath the shutters which would prevent their complete closure after operation. It is recommended confirmation is sought that the shutter is linked to the fire alarm system or operated by fusible links. |  | Maintenance | Priority 2 1 Month
10 | All Areas | An emergency lighting system was apparent however additional emergency lighting is required to be located in accordance with British Standard 5266. | Staff/Visitors | 2 | High | An emergency lighting system was apparent however additional emergency lighting is required to be located on the main entry/exit to the Pre-School and in the Disabled Toilet in accordance with British Standard 5266 to provide illumination for occupants in the event of a fire. |  | Management Procedure | Priority 2 1 Month
11 | External Escape Route | No external emergency lighting was sited. | Staff/Visitors | 2 | High | At the time of the assessment it appeared that insufficient artificial lighting in the form of street lighting is available adjacent the premise. However this should be confirmed during periods of darkness and external Emergency Light Luminaries sited if required. |  | Management Procedure | Priority 2 1 Month
12 | Main Entrance | “NO SMOKING” signs are required to be posted at the entrance to the building. | Staff/Visitors | 2 | High | “NO SMOKING” signs are required to be posted at the entrances to the building to ensure persons are instructed as to their responsibility by law not to smoke in the premise. |  | Site Signage | Priority 2 1 Month
13 | Pre-School | Fire Doors require smoke seals to ensure the doors comply with the definition 'fire resisting' as defined by British Standard 476. The Fire Door adjacent the Disabled Toilet to the Pre-School required smoke seals. | Staff/Visitors | 2 | High | Approved smoke seals and intumescent strips are required to be fitted to the top and both edges of all fire doors to prevent the passage of smoke and fire putting persons/premises at risk. The Fire Door adjacent the Disabled Toilet to the Pre-School required smoke seals to ensure the door complies with the definition 'fire resisting' as defined by British Standard 476. |  | Maintenance | Priority 2 1 Month
14 | Kitchen | “Fire Door Keep Shut” signage was required on the door to the kitchen as the current signage was incorrect. | Staff/Visitors | 2 | High | All fire resisting self-closing doors are to be permanently marked on each side at eye level with a blue circular notice bearing the words “Fire Door Keep Shut”. Signage in accordance with the standards set out in British Standard 5499 was required on the door to the kitchen as the current signage was incorrect. |  | Site Signage | Priority 2 1 Month
15 | Fire Alarm Panel | The fire alarm panel is inadequately sited as it is currently located in the electrical cupboard. | Staff/Visitors | 2 | High | The fire alarm panel is inadequately sited as it is currently located in the electrical cupboard. Fire alarm panels are to be easily accessible and located close to the main entrance installed to the requirements of British Standard 5839 part 1. |  | Management Procedure | Priority 2 1 Month
16 | All Areas | It was noted there is no zone plan by the fire alarm panel in accordance with BS5839-1:2013 | Staff/Visitors | 2 | High | There is no zone plan by the fire alarm panel. BS5839-1:2013 states that zone plans are required on every system of any size, and should also be noted as a major non-compliance during routine maintenance, when they are not displayed on existing installations. |  | Management Procedure | Priority 2 1 Month
17 | Kitchen | The Co2 fire extinguisher in the kitchen was found to be freestanding. | Staff/Visitors | 2 | High | It is recommended that arrangements are made to have the Co2 fire extinguisher in the kitchen hung on a bracket or placed within a floor stand which is affixed to the wall and signed accordingly. |  | Management Procedure | Priority 2 1 Month
18 | All Areas | Written appropriate fire procedures require initiating and updating regularly. | Staff/Visitors | 2 | High | It should be ensured a written fire plan is initiated and augments the existing fire action notices which are affixed to walls in the premises. This plan should then be available as a training document. |  | Management Procedure | Priority 2 1 Month
19 | Fire Assembly Point | A Fire Assembly Point has been nominated and signed however is required to be highlighted in the Fire Plan. | Staff/Visitors | 2 | High | It is recommended a single Fire Assembly Point is designated and documented within the Fire Plan. All staff should then be instructed on the location of the Fire Assembly Point. |  | Management Procedure | Priority 2 1 Month
20 | All Areas | No adequate procedures for evacuation/assisting occupants with disabilities were evident. | Staff/Visitors | 2 | High | Under the Equality Act, if disabled people could realistically expect to use the service, which you provide, then you must anticipate any reasonable adjustments that could make it easier for that right to be exercised. Accordingly if disabled people are going to be in your premise, then you must also provide safe means for them to leave if a fire occur. Any disabled person in the premises could be at risk unless suitable disability procedures are devised, which take all issues and staff into account and are understood by all appropriate staff members. |  | Management Procedure | Priority 2 1 Month
21 | All Areas | No conformation of a written procedure for end of day building inspection was available. | Staff/Visitors | 2 | High | Confirm end of day building inspection procedures are in place. If required formulate written procedure for end of day building inspection. |  | Include in Fire Plan | Priority 2 1 Month
22 | All Areas | No written routine in house fire inspections are evident. | Staff/Visitors | 2 | High | Written instruction on Fire Alarm, Emergency Lighting, Fire Extinguishers and Means of Escape custodian checks and tests is required to be formulated. |  | Management Procedure | Priority 2 1 Month
23 | All Areas | No procedure for the training of new arrivals was evident. | Staff/Visitors | 2 | High | It is particularly important that management ensure that all newly appointed or temporary staff are made aware of the means of escape and fire procedures at the commencement of their employment. Suitable records of training should be maintained within the Fire Logbook |  | Management Procedure | Priority 2 1 Month
24 | All Areas | No Fire Training has been carried out. | Staff/Visitors | 2 | High | All persons at work should be instructed and trained to ensure that they understand the fire emergency plan and fire precautions in the premises and the action to be taken in the event of fire. In addition, certain categories of staff should be instructed and trained in matters which are their particular responsibilities. Suitable records of training should be maintained within the Fire Logbook. |  | Management Procedure | Priority 2 1 Month
25 | All Areas | No fire drills have been carried out | Staff/Visitors | 2 | High | A practice fire drill should be carried out at least once and preferably twice each year simulating conditions in which one of the escape routes from the building is considered to be unavailable. During these drills the fire alarm should be operated by a member of staff who is told of a supposed outbreak of fire, and thereafter the fire routine should be rehearsed as fully as circumstances allow. Suitable records of training should be maintained within the Fire Logbook. |  | Management Procedure | Priority 2 1 Month
26 | All Areas | No documentation for the weekly managerial checks of the Fire Alarm system was produced. | Staff/Visitors | 2 | High | It is recommended that the fire alarm system is tested by management on a weekly basis preferably at the same time and on the same day each week. These tests should be recorded in the Fire Logbook. |  | Management Procedure | Priority 2 1 Month
27 | All Areas | No documentation was available for the installation of the fire alarm system. | Occupants/Visitors | 2 | High | It is recommended that a check is made with the installation company to confirm that they have provided a certificate of installation and commissioning which is then to remain on site within the Fire Logbook and that they or another competent contractor are engaged in a servicing contract to maintain and service the system in accordance with British Standard 5839 pt 1. |  | Management Procedure | Priority 2 1 Month
28 | All Areas | No evidence for the monthly managerial checks of the emergency lighting system was produced. | Staff/Visitors | 2 | High | It is recommended that monthly tests are carried out by management on the emergency lighting system by the simulation of a failure of the power supplies. The results of these tests should be recorded in the Fire Logbook. Any failure of luminaries etc. should be recorded and arrangements made to provide the necessary repairs. |  | Management Procedure | Priority 2 1 Month
29 | All Areas | No documentation was available for the installation of the emergency lighting system. | Occupants/Visitors | 2 | High | It was apparent that the emergency lighting system was fairly recently installed. It is recommended however, that a check is made with the installation company to confirm that they have provided a certificate of installation and commissioning which is then to remain on site within the Fire Logbook and that they or another competent contractor are engaged in a servicing contract to maintain and service the system in accordance with British Standard 5266. |  | Management Procedure | Priority 2 1 Month
30 | All Areas | No evidence for the monthly managerial checks of the fire extinguishers was produced. | Staff/Visitors | 2 | High | It is recommended that monthly recorded managerial checks are initiated which should ensure that the fire extinguishers provided are in position and available for use at all times and not obscured/obstructed by storage or refuse. These checks should be recorded within the Fire Logbook. |  | Management Procedure | Priority 2 1 Month
31 | All Areas | Weekly managerial checks of the Fire Shutter in the kitchen is required in conjunction with the Fire Alarm system tests. | Staff/Visitors | 2 | High | It is recommended that the operation of the electronic Fire Shutter in the kitchen is tested on a weekly basis and that it is serviced in accordance with the manufacturers recommendations. Tests and servicing should be recorded in the Fire Logbook. |  | Management Procedure | Priority 2 1 Month
32 | All Areas | No evidence for the routine in-house premises fire inspections was produced. | Staff/Visitors | 2 | High | Fire doors, exit routes and exit doors should be checked regularly and suitable records of testing and maintenance should be maintained within the Fire Logbook. An inspection of the area of responsibility is to be carried out with particular attention to - fire doors opening and closing correctly, smoke seals on fire doors are not damaged, there is a clear exit route from anywhere in the building and externally to a place of safety, fire exits open easily and fully, no build up of combustible materials is evident and no obvious hazardous ignition sources exist. |  | Management Procedure | Priority 2 1 Month
33 | All Areas | It is recommended that a dedicated Fire Logbook is initiated, in which all fire related records should be maintained. | Staff/Visitors | 2 | High | It is recommended that a dedicated Fire Logbook is initiated, in which all fire related records should be maintained. The Fire Logbook records remind management to complete regular training, tests and checks. Failure to carry out the tests etc. could result in increased risk due to failure of the fire precautionary arrangements in an emergency. |  | Management Procedure | Priority 2 1 Month
34 | All Areas | The managerial control of contractors is inadequate. | Staff /Visitors | 3 | Medium | A Fire Safety Policy regarding any contractors on site should be initiated. Fire safety information to be given to contractors working on the premises including the introduction of Hot Work Permits should be given consideration. |  | Management Procedure | Priority 3 3 Months
35 | All Areas | The fire alarm system was not monitored. | Staff /Visitors | 3 | Medium | Should a fire start outside of the normal working hours of the establishment, it would be liable to develop unnoticed and result in very severe damage to the property placing life at risk, with unavoidable consequences for the premise. Remote monitoring of the fire alarm system would provide early detection of a fire. |  | Management Procedure | Priority 3 3 Months
36 | All Areas | Provisions to encounter arson have been considered. Occupants should be vigilant to the dangers, which an arson attack would pose. | Staff /Visitors | 3 | Medium | Half of all the large fire’s that occur are the result of arson, and good security and Fire Prevention can help prevent or reduce the severity of an arson attack. Occupants should be vigilant to the dangers, which an arson attack would pose. |  | Management Procedure | Priority 3 3 Months

## RA Part 4
FIRE RISK ASSESSMENT ACTION PLAN
Company: |  | Chearsley Village Hall |  |  | FRA 1 Annual Inspection
Location |  | Winchendon Road, Chearsley, Buckinghamshire, HP18 0DP |  |  | FRA 2 - Review
Assessor |  | Dave Perkins MIFPO MInstLM
Ref | Site Location | Action |  | Action Taken |  | Actioned By | Date
1 | Electrical Cupboard | It was noted that the electrical cupboard contained combustibles. | It was noted that the electrical cupboard contained combustibles. | Pre-school alerted and as many combustibles as possible removed from the plant room to outside storage container. Area secured with lock and key to prevent unauthorised access. Weekly checks are done to ensure all storage remains at least 1m from utilities. Plumber consulted who deemed the area a very low fire risk. Insurance company also alerted in February 2019. |  | Antonia Stratford | May 2018 and ongoing
2 | Electrical Cupboard | The compartment fire walls in the Electrical Cupboard required compartmentation and smoke stopping. | The compartment fire walls in the Electrical Cupboard required compartmentation and smoke stopping. | Complete |  | Antonia Stratford | 2018-06-01
3 | Pre-School | The main entry/exit to the Pre-School is an escape route however it contained combustibles and obstructions. It is recommended the area adjacent the main entry/exit to the Pre-School is kept clear. | The main entry/exit to the Pre-School is an escape route however it contained combustibles and obstructions. It is recommended the area adjacent the main entry/exit to the Pre-School is kept clear. | Pre-school alerted and all efforts are made to keep entry/exit routes clear at all times |  | Antonia Stratford | 2018-06-01
4 | All Areas | The electrical safety testing (PAT) of electrically powered appliances is required. | The electrical safety testing (PAT) of electrically powered appliances is required. | PAT testing carried out annually on all hall owned electrical equipment and pre-school equipment |  | Ruth Holland | TBC
5 | All Areas | It is recommended there should be a written policy regarding the managerial control of mains-powered electrical items of equipment that are brought into the premise. | It is recommended there should be a written policy regarding the managerial control of mains-powered electrical items of equipment that are brought into the premises. | The written policy is in our terms and conditions. These state that it is the responsibility of hirers to ensure that all electrical equipment brought into the hall and used during the period of hire has been safety checked by a qualified electrician. |  | Hirers | Ongoing
6 | Kitchen | Although recently installed it should be ensured the oven and other catering equipment is regularly checked for defects and is cleaned regularly with documentation held on-site. | Although recently installed it should be ensured the oven and other catering equipment is regularly checked for defects and is cleaned regularly with documentation held on-site. | The oven and other catering equipment is checked after each hire and cleaners also clean the kitchen and equipment on a weekly basis. |  | All and cleaner | Ongoing
7 | All Areas | No lightning conductor for the building was evident. | No lightning conductor for the building was evident. | This was checked with project manager Philip Ellis at the end of the new hall build and deemed not necessary. |  | Antonia Stratford | 2018-05-01
8 | All Areas | The main electrical system has been installed recently however no documentation was available. | The main electrical system has been installed recently however no documentation was available. | Documentation now available in the hall files which are in the kitchen cupboard |  | Antonia Stratford | 2018-05-01
9 | Kitchen | The kitchen is provided with a serving hatch with a fire shutter installed to provide a barrier against the spread of fire between areas of the building in order to limit damage to the building however it should be confirmed the shutter is linked to the fire alarm system or operated by fusible links. | The kitchen is provided with a serving hatch with a fire shutter installed to provide a barrier against the spread of fire between areas of the building in order to limit damage to the building however it should be confirmed the shutter is linked to the fire alarm system or operated by fusible links. | Shutter is linked to the fire alarm and documentation is filed in the hall files which are in the kitchen cupboard |  | Antonia Stratford | 2018-05-01
10 | All Areas | An emergency lighting system was apparent however additional emergency lighting is required to be located in accordance with British Standard 5266. | An emergency lighting system was apparent however additional emergency lighting is required to be located in accordance with British Standard 5266. | Emergency lighting now installed and fully compliant |  | Antonia Stratford | 2018-08-01
11 | External Escape Route | No external emergency lighting was sited. | No external emergency lighting was sited. | Emergency lighting now installed and fully compliant |  | Antonia Stratford | 2018-08-01
12 | Main Entrance | “NO SMOKING” signs are required to be posted at the entrance to the building. | “NO SMOKING” signs are required to be posted at the entrance to the building. | Completed |  | Antonia Stratford | 2018-06-01
13 | Pre-School | Fire Doors require smoke seals to ensure the doors comply with the definition 'fire resisting' as defined by British Standard 476. The Fire Door adjacent the Disabled Toilet to the Pre-School required smoke seals. | Fire Doors require smoke seals to ensure the doors comply with the definition 'fire resisting' as defined by British Standard 476. The Fire Door adjacent the Disabled Toilet to the Pre-School required smoke seals. | Completed |  | Antonia Stratford | 2018-06-01
14 | Kitchen | “Fire Door Keep Shut” signage was required on the door to the kitchen as the current signage was incorrect. | “Fire Door Keep Shut” signage was required on the door to the kitchen as the current signage was incorrect. | Completed |  | Antonia Stratford | 2018-06-01
15 | Fire Alarm Panel | The fire alarm panel is inadequately sited as it is currently located in the electrical cupboard. | The fire alarm panel is inadequately sited as it is currently located in the electrical cupboard. | Discussed with builders and project manager and decided not to move panel as deemed not necessary and disruptive to the fabric of the building. |  | Antonia Stratford | 2018-06-01
16 | All Areas | It was noted there is no zone plan by the fire alarm panel in accordance with BS5839-1:2013 | It was noted there is no zone plan by the fire alarm panel in accordance with BS5839-1:2013 | Deemed not necessary as the hall is all on one level and is only 1 large room, store room, office, a kitchen and toilets. |  | Antonia Stratford | 2018-06-01
17 | Kitchen | The Co2 fire extinguisher in the kitchen was found to be freestanding. | The Co2 fire extinguisher in the kitchen was found to be freestanding. | Now contained in a floor bracket |  | Alex Wall Morris | 2018-06-01
18 | All Areas | Written appropriate fire procedures require initiating and updating regularly. | Written appropriate fire procedures require initiating and updating regularly. | Written and updated in February 2019 |  | Antonia Stratford | 2019-02-01
19 | Fire Assembly Point | A Fire Assembly Point has been nominated and signed however is required to be highlighted in the Fire Plan. | A Fire Assembly Point has been nominated and signed however is required to be highlighted in the Fire Plan. | Fire Assembly Point is the playground in hall grounds |  | Antonia Stratford | 2019-02-01
20 | All Areas | No adequate procedures for evacuation/assisting occupants with disabilities were evident. | No adequate procedures for evacuation/assisting occupants with disabilities were evident. | Now contained in the fire policy/plan |  | Antonia Stratford | 2019-02-01
21 | All Areas | No conformation of a written procedure for end of day building inspection was available. | No conformation of a written procedure for end of day building inspection was available. | It is the responsibility of the hirer to ensure that the building is left in a safe and clean condition. Bookings secretary and other members of the committee will also check from time to time. |  | Antonia Stratford | 2019-02-01
22 | All Areas | No written routine in house fire inspections are evident. | No written routine in house fire inspections are evident. | Fire Log Book now in place
23 | All Areas | No procedure for the training of new arrivals was evident. | No procedure for the training of new arrivals was evident. | New members of the committee will be alerted to the fire policy and checks |  | Antonia Stratford | 2019-02-01
24 | All Areas | No Fire Training has been carried out. | No Fire Training has been carried out. | It is the responsibility of the hirer to ensure that the hall fire policy is adhered to.
25 | All Areas | No fire drills have been carried out | No fire drills have been carried out | It is the responsibility of the hirer to ensure that the hall fire policy is adhered to.
26 | All Areas | No documentation for the weekly managerial checks of the Fire Alarm system was produced. | No documentation for the weekly managerial checks of the Fire Alarm system was produced. | Now being recorded in a Fire Log Book which is available to view in the kitchen. |  | Martin Hearmon | 2019-02-01
27 | All Areas | No documentation was available for the installation of the fire alarm system. | No documentation was available for the installation of the fire alarm system. | In hall files which are in the kitchen cupboard |  | Antonia Stratford | 2019-02-01
28 | All Areas | No evidence for the monthly managerial checks of the emergency lighting system was produced. | No evidence for the monthly managerial checks of the emergency lighting system was produced. | Now being recorded in a Fire Log Book which is available to view in the kitchen. |  | Martin Hearmon | 2019-02-01
29 | All Areas | No documentation was available for the installation of the emergency lighting system. | No documentation was available for the installation of the emergency lighting system. | In hall files which are in the kitchen cupboard |  | Antonia Stratford | 2019-02-01
30 | All Areas | No evidence for the monthly managerial checks of the fire extinguishers was produced. | No evidence for the monthly managerial checks of the fire extinguishers was produced. | Now being recorded in a Fire Log Book which is available to view in the kitchen. |  | Martin Hearmon | 2019-02-01
31 | All Areas | Weekly managerial checks of the Fire Shutter in the kitchen is required in conjunction with the Fire Alarm system tests. | Weekly managerial checks of the Fire Shutter in the kitchen is required in conjunction with the Fire Alarm system tests. | Now being recorded in a Fire Log Book which is available to view in the kitchen. |  | Martin Hearmon | 2019-02-01
32 | All Areas | No evidence for the routine in-house premises fire inspections was produced. | No evidence for the routine in-house premises fire inspections was produced. | N/A
33 | All Areas | It is recommended that a dedicated Fire Logbook is initiated, in which all fire related records should be maintained. | It is recommended that a dedicated Fire Logbook is initiated, in which all fire related records should be maintained. | Now in progress |  | Antonia Stratford | 2019-02-01
34 | All Areas | The managerial control of contractors is inadequate. | The managerial control of contractors is inadequate. | It is the responsibility of the hirer to ensure that the hall fire policy is adhered to. |  | Antonia Stratford | 2019-02-01
35 | All Areas | The fire alarm system was not monitored. | The fire alarm system was not monitored.
36 | All Areas | Provisions to encounter arson have been considered. Occupants should be vigilant to the dangers, which an arson attack would pose. | Provisions to encounter arson have been considered. Occupants should be vigilant to the dangers, which an arson attack would pose. | Intruder alarm now in place |  | Antonia Stratford | 2019-02-01